2.3 IWMAC Checklist – N2 / N2 Open

For Kiona to be able to integrate a device into IWMAC on N2/N2 Open, some information is needed to ensure everything functions as it should. It is not possible to "scan" the devices or data points, so the customer must prepare a topology/list of networks and serial loops as well as detailed tag lists.

There must be sufficient parameters for the basic functions of a top system to be fulfilled (Operation/Fault/Frost/Calendar/Temperatures/Setpoint, etc.).

Depending on the equipment to be integrated, some variations in the supporting data are requested.

For each parameter to be integrated, the following information is required:

- Description with system, component code and descriptive text – see document "1 – Design and Integration Guide"

- Unit of measurement (%, °C, etc.)

- Status text (0=Off 1=On 2=Auto, 0=Normal 1=Fault, etc.)

- Read/Read-Write

N2 – Johnson DX specifically (SYS91/Metasys)

- Internal points in regulators must be specified in the parameter lists if they are to be integrated. If IWMAC is e.g. to control the installation with its top system calendar on DCO1, this must be specified.

- It is not sufficient to specify only analogue/digital inputs and outputs. Internal points must also be stated to include setpoints, curves, switches, alarms on sensors, etc.

- Parameter lists for Johnson DX must contain N2 protocol addresses (according to Johnson documentation, e.g.: AI1, XT3DI1, PM10K02, OUT1, HIA1, AIH1, etc.).

N2 Open – Johnson FX specifically

- It is not sufficient to submit the .prn file for setting up an FX regulator, as this contains too few characters and too little information to obtain a good explanation of the various parameters.

- If ADI points with bits are used, these must be specified particularly in the parameter list.

- Parameter lists for Johnson FX set up in Excel must contain N2 protocol addresses (adf1, adi1, bd1, adi1, bit1).

| Checklist – N2 device integration |  | Device:____________________ |
| --- | --- | --- |
| Checkpoint | Explanation | Done (Yes/No) |
| Check the number of devices and refresh rate | An assessment has been made of the number of devices on serial loops to ensure the refresh rate for parameters will not be too low (should not take several minutes). |  |
| Check addresses and communication setup | All serial devices on a loop have unique slave addresses and a similar communication setup in general. Baudrate, data bits and stop bits, parity. |  |
| The device(s) have been fully commissioned and function tested. |  |  |
| Bus topology with all devices has been submitted. | Slave addresses, communication settings, IP addresses, COM ports, media converters, etc. are described. |  |
| Tag list | Complete tag list has been prepared as described in this guide and submitted to Kiona. |  |