2.4 IWMAC Checklist – KNX via NETxOPC server

For Kiona to be able to integrate KNX into IWMAC, some information is needed to ensure everything functions as it should. It is not possible to "scan" the devices or data points, so the customer must export and transfer the necessary data from ETS (the programming tool).

Before the installation is programmed, a group address structure and naming must be submitted to Kiona for review and approval, to ensure images can be linked effectively.

Before integration can start, Kiona must have received all the information specified in the checklist below. All parameters should be named in a way that makes them easily identifiable; see document "1 – Design and Integration Guide".

An Excel file with supplementary information must contain the following 7 additional columns beyond the data from the *.esf file:

- Writable parameters (rw)

- Unit of measurement (°C, m3/h, %, etc.)

- Scaling (0–255=0–100, etc.)

- Gateway/IP (to distinguish which parameters belong to which gateways)

- Alarm priority (A–B–C). A is highest priority and will normally be sent by SMS to the alarm monitor

- Normally closed/NC (0=Alarm, 1=OK)

- Read on OPC boot (Read on reconnect)

The KNX installation must have been commissioned and tested in advance before Kiona can import the parameter list.

| Checklist – KNX integration |  | Device:____________________ |
| --- | --- | --- |
| Checkpoint | Explanation | Done (Yes/No/-) |
| Group address structure has been clarified and approved by Kiona. | The structure is also adapted for efficient linking of room control images. |  |
| All parameters are named in accordance with "1 – Design and Integration Guide", or alternatively discussed with and approved by Kiona. |  |  |
| All components of the bus have been fully commissioned and function tested. |  |  |
| Kiona has been notified of how many data points are to be integrated. | Licence for the number of data points and number of gateways. |  |
| Topology showing each gateway with underlying bus lines and addresses. |  |  |
| Excel sheet with the necessary information beyond the ESF file contents has been created and submitted to Kiona. |  |  |
| *.esf file from ETS, cleaned of parameters not to be integrated, has been submitted to Kiona. | Reconciled with the number of points stated at time of licence order. |  |
| An overview of the desired top system calendars and which data points they should write to has been submitted to Kiona. | Operating times must be known if Kiona is to enter them. |  |