2.5 IWMAC Checklist – OPC DA

For Kiona to be able to integrate a device into IWMAC on OPC, some information is needed to ensure everything functions as it should. It is not possible to "scan" the devices or data points, so the customer must prepare detailed tag lists.

It is often challenging to establish communication where an OPC server is placed on another computer on the network, especially if it is also on a different technical network and the network is domain-controlled, etc. As a general rule, Kiona therefore needs to know whether the OPC server can be installed on an IWMAC PC.

OPC connection information

- The connection string for the OPC server (the OPC server name to be used for our OPC client).

- Any username and password the client must use to connect to the OPC server.

- Group address name and access path if the OPC server requires this.

- If the server is installed on a PC other than an IWMAC PC, the customer must provide an overview of all relevant parameters to be set for the DCOM configuration, as well as the machine name, network parameters such as IP address, username and password for the account running and administering the OPC server.

- The number of communication threads supported in parallel by the OPC server and each device behind it must be specified.

Parameter list

- Unique name and description of the point. This text must clearly identify a point in relation to other corresponding points on corresponding and other systems, e.g. a cross-disciplinary labelling system (TFM) and component code.

- OPC registry address and data type and data length; see table.

| Value (decimal) | Data type | Description |
| --- | --- | --- |
| 0 | VT_EMPTY | Default/Empty (Nothing) |
| 2 | VT_I2 | 2-byte signed integer |
| 3 | VT_I4 | 4-byte signed integer |
| 4 | VT_R4 | 4-byte real |
| 5 | VT_R8 | 8-byte real |
| 6 | VT_CY | Currency |
| 7 | VT_DATE | Date |
| 8 | VT_BSTR | Text |
| 10 | VT_ERROR | Error code |
| 11 | VT_BOOL | Boolean (TRUE = -1, FALSE = 0) |
| 17 | VT_I1 | 1-byte signed character |
| 18 | VT_UI1 | 1-byte unsigned character |
| 19 | VT_UI2 | 2-byte unsigned integer |
| 20 | VT_UI4 | 4-byte unsigned integer |
| +8192 | VT_ARRAY | Array of values (e.g. 8200 = array of text values) |

- Any bit specification if a single bit in a register is to be exported as a binary data point.

- "Engineering unit" such as degC, bar, Pa, % and equivalent for analogue values.

- Scaling must be specified if relevant. Is the decimal point to be moveable on an integer value: x10, x0.1, x0.001, etc.?

- All statuses represented by Boolean or integer values, e.g. 0=Off, 1=On.

- Clear description of whether the point is readable or writable: r for readable, rw for also writable.

- Alarm level classification for digital alarms: A is highest and sent as alarm message, B and C are lower levels.

All units behind the OPC installation must have been commissioned and tested in advance before Kiona can import the parameter list.

| Checklist – OPC-DA integration |  | Server:____________________ |
| --- | --- | --- |
| Checkpoint | Explanation | Done (Yes/No) |
| All parameters are named in accordance with "1 – Design and Integration Guide", or alternatively discussed with and approved by Kiona. |  |  |
| All components of the bus have been fully commissioned and function tested. |  |  |
| The customer has tested access to the OPC server with an OPC client installed on an IWMAC PC. | Confirmation that OPC connectivity is working and that communication with all devices behind it is working. |  |
| Connection information has been submitted to Kiona. |  |  |
| The complete tag list has been prepared as described in this guide and submitted to Kiona. |  |  |
| An overview of the desired top system calendars and which data points they should write to has been submitted to Kiona. | Operating times must be known if Kiona is to enter them. |  |