3.1 IWMAC Checklist – Ventilation

For Kiona to be able to ensure the IWMAC visualisation we provide is correct, we need to receive adequate and accurate documentation. The aim is to create a simple, clear and understandable system for the end user of the installation.

At a minimum, the following must be included in the submitted documentation:

- System number e.g. 36.01, 360.01, 360.001 and description of operating area e.g. warehouse, office, workshop.

- Installation-specific functional description, outlining at least the following:

- Type of temperature regulation, e.g. constant supply-air temperature, outdoor-air compensated supply-air regulation.

- Type of fan regulation, e.g. constant airflow, constant pressure.

- Any active functions and associated setpoints, e.g. recirculation air, night cooling, extended operation.

- Connected extra modules and their settings/active function.

- Curves for seasonal compensation of air or temperature, etc.

- Outdoor temperature. Activation/deactivation of functions and their setpoints.

- Calendar functions for activating/deactivating functions.

- Interlocks, changes in types of regulation depending on outdoor temperature, dates, etc.

- System diagram – flowchart with component codes entered; the supporting data must be "as-built".

- A decision must be made as to whether clock time control from the automation is preferred or whether IWMAC is to set up a top system calendar.

- If a top system calendar is used, Kiona must be informed about which parameters to use for start/stop and the relevant times.

- If there is no dedicated point for a clock timer and IWMAC is to use the installation's system selector switch, IWMAC will create a virtual software selector switch for use in the image display.

- If the clock timer in the automation is used, IWMAC will try to mirror this as far as possible. There may be certain special cases where this presents challenges.

If a top system calendar is chosen, bear in mind that the clock timer in the automation must be disabled. Kiona also needs to know whether all functions (night cooling, recirculation air, etc.) are handled using the parameter that the top system calendar will use.

The checklist below applies to each ventilation system (system number).

| Checklist – ventilation unit |  | System no.:_____________________ Device:________________________ |
| --- | --- | --- |
| Checkpoint | Explanation | Done (Yes/No) |
| System diagram with all component codes has been sent to Kiona, with "as-built" component location. |  |  |
| Codes on the system diagram are also in the parameter list. |  |  |
| Alternatively, IWMAC labelling is used in images. |  |  |
| IWMAC top system calendar control is to be used. |  |  |
| Alternatively, the regulator's internal clock timer is used. |  |  |
| Functional description with information as requested above has been sent to Kiona. |  |  |
| Points on the checklist for the communication protocol have been dealt with. |  |  |
| Any additional functions, such as weather forecast, power monitor, measured value distribution, alarm functions and similar, are set out in written supporting documentation. | Remember to order smart functions if necessary. |  |