3.6 IWMAC Checklist – EOS (Energy Monitoring System)

For Kiona to be able to set up a clear and accurate EOS in IWMAC, we need to have a good picture of how the customer wants to visualise the energy setup.

- All physical meters must have been implemented and commissioned on the installation.

- A quality assurance procedure must be undertaken, confirming that the physical meter and IWMAC show the same value.

- A decision must be made on how to group the tree structure and which calculations are required.

- Kiona must receive a list of the meters with labelling, plus an indication of the group in which the customer wants them presented. See document "1 – Design and Integration Guide".

- It is also important to specify the device from which the measured value is to be taken (PLC, meter, district heating plant, etc.). See "IWMAC TEMPLATE 06 – EOS.xltx".

When selecting multiple meters/groups of meters in EOS, the key point to note is that all parameters specified under these will be totalled in the system (Energy/Volume/Persons/Area).

A clear strategy is therefore needed on how to group meters and at what level in the system persons/area should be specified in order to avoid these being totalled multiple times in the same group.

This requires the customer to decide how they wish to use the system and what data they want to extract at the different levels. The structure should then be planned on this basis.

For Kiona to be able to present an energy/temperature graph, there must be an outdoor temperature available for this purpose.

| Checklist – EOS |  |  |
| --- | --- | --- |
| Checkpoint | Explanation | Done (Yes/No) |
| All calculations to be made have been documented and submitted to Kiona. |  |  |
| All key indicators have been submitted to Kiona. | Persons per area, area for each building section, etc. See EOS template. |  |
| Clarification has been reached with Kiona as to which reports can be extracted. |  |  |
| Meter structure submitted to Kiona. |  |  |
| Measured values on all meters have been checked and approved. |  |  |