## Readme
About this template Sheet "Parameterlist" All Modbus-information and "per parameter" configuration goes into this sheet. The sheet is split into three parts, where first part is for creating the vieweable parameter-name in IWMAC. The second part is modbus protocol related information for the driver to work. This includes register type, function code, modbus address and swapping-functions. The last part is used for additional nescesarry presentation-related information for IWMAC supermarket, graph etc., eg. engineering units to the parameters, scaling, setting texts on numerical states, scaling of raw values, setting alarm-levels and such. Many of the columns have their own "Comments" with helpful information of how they should be filled in. Sheet "State-Texts" If textual states is wanted on integer and boolean parameters, they have to be added in this sheet with an reference. Afterwards, you will be able to select the references for the parameters of interest in "Parameterlist"-sheet. Sheet "Scale" If any modbus register's raw-value need some sort of scaling before presentation the factors can be added in this sheet with references. The references will then be usable in the "Parameterlist"-sheet.

## Parameterlist
[23 empty] | Datatype | register | Beskrivelse | informativt, MODBUS rw flag | lese_skrive | Alarmnivå |  | Funksjonskoder
Parameter naming |  |  | Modbus settings | [8 empty] | IWMAC presentation | [9 empty] | 0x coil status | BOOL | [5 empty] | Ikke alarmerbart
System code, building addressing etc. (Section A) | Component and functional code (Section B) | Description (Section C) | Data type | Function code for reading | Function code for writing | Register type | Register address | (start) bit 0..15 (16bit) 0..31 (32bit) | Antall bit i nibble 2..16 | Byte swap | Word swap | Range min | Range max | Scale reference | Num decimal | Engineering unit | read/write attribute | Alarm level | State-text reference | Parameter grouping | Descriptions / comments | 1x input status | UINT16 | 0x | 0x Discrete Output Coils | rw | r | A | A-Alarm = SMS | Generelt:
Ahu01 | FanSup-Cmd | Supply fan command | BOOL | 02 Read Input Status |  | 1x input status | 0 | [9 empty] | r |  | OnOff | AHU Floor 1 |  | 3x Input register | SINT16 | 1x | 1x Discrete Input Contacts | r | rw | B | B-alarm | SP | Settpunkt
Ahu01 | FanSup-Alm | Supply fan Fault | BOOL | 02 Read Input Status |  | 1x input status | 1 | [9 empty] | r | A | NormalAlarm | AHU Floor 1 |  | 4x holding register | UINT32 | 3x | 3x Analoge Input Registers | r |  | C | C-alarm | PV | prosessverdi | Måleverdi som går på regulatorinngang
Ahu01 | FanSup-ManSwi | Sup. Fan Operation mode switch | UINT16 | 03 Read Holding Registers | 06 Preset Single Register | 4x holding register | 0 | [9 empty] | rw |  | AutoOffOn | AHU Floor 1 |  |  | SINT32 | 4x | Analoge Holding Registers | rw |  | N | Inaktiv alarm, kan aktiveres av bruker senere | MV | Måleverdi | Måleverdi som kun er til alarmering, avlesning, logging
Ahu01 | FanEx-raw | Data Word | UINT16 | 03 Read Holding Registers | 06 Preset Single Register | 4x holding register | 1 | M | [8 empty] | rw |  |  | Motherwords |  |  | FLOAT32 |  |  |  |  | !A |  | C | analog utgang
Ahu01 | FanEx-Cmd | Extract fan command | BOOL |  |  |  | 1 | 0 | [8 empty] | r |  | OnOff | AHU Floor 1 |  |  | FLOAT64 |  |  |  |  | !B |  | KMD | Digital utgang
Ahu01 | FanEx-Alm | Extract fan Fault | BOOL |  |  |  | 1 | 1 | [8 empty] | r | A | NormalAlarm | AHU Floor 1 |  |  | UINT64 |  |  |  |  | !C |  | FEIL | Digital inngang feilsignal
Ahu01 | FanSEx-ManSwi | Ext. Fan Operation mode switch | UINT16 |  |  |  | 1 | 2 | 2 | [7 empty] | rw |  | AutoOffOn | AHU Floor 1 |  |  | SINT64 |  |  | 01 Read Coil Status |  |  |  | VERN | Digital inngang motorvern
Ahu01 | SupTemp | Supply temperature | UINT16 | 04 Read Input Registers |  | 3x Input register | 0 |  |  |  |  | -50 | 120 | x0.1 | 1 | °C | r |  |  | AHU Floor 1 | raw-value is divided by 10 for analog representation |  | DOUBLE |  |  | 02 Read Input Status |  |  |  | REV | Digital inngang sikkerhetsbryter
Ahu01 | SupTempSet | Supply temperature setpoint | UINT16 | 03 Read Holding Registers | 06 Preset Single Register | 4x holding register | 2 |  |  |  |  | 15 | 35 | x0.1 | 1 | °C | rw |  |  | AHU Floor 1 | raw-value is divided by 10 for analog representation |  |  |  |  | 03 Read Holding Registers |  |  |  | STA | Digital inngang status/tilbakemelding
Ahu01 | HVlv-Level | Heating valve opening level | FLOAT32 | 04 Read Input Registers |  | 3x Input register | 1 |  |  | Y |  | 0 | 100 |  |  | % | r |  |  | AHU Floor 1 | [5 empty] | 04 Read Input Registers |  |  |  | SW_BR | programvarepunkt anleggsvender
Ahu01 | RHX-Level | Rotating heat exh. Level | FLOAT32 | 04 Read Input Registers |  | 3x Input register | 3 |  |  | Y |  | 0 | 100 |  |  | % | r |  |  | AHU Floor 1 | [9 empty] | SW_UR | sprogramvarepunkt ur
[30 empty] | A | alarmverdi
[30 empty] | AL | alarmverdi
[30 empty] | RST | resettpunkt
[30 empty] | G | Forsterkning
[30 empty] | PB | Proposjonalbånd
[30 empty] | I | I-tid
[30 empty] | d | D-tid
05 Force Single Coil
[26 empty] | 06 Preset Single Register |  |  |  | Romkontroll:
[26 empty] | 15 Force Multiple Coils |  |  |  | basSP | basis-sp SD-anlegg
[26 empty] | 16 Preset Multiple Regs |  |  |  | aktSP | aktuelt settpunkt
[30 empty] | lokOffsSP | Lokal forsering sp +/- x°C
[30 empty] | DrMod | driftsmodus natt,prekomfort,komfort e.l.
[30 empty] | V | varmeutgang
[30 empty] | K | kjøleutgang
Note on B4: The viewable parametername will be generated as: Section A_Section B [Section C]
Note on J5: Add Motherword on the line above parameter-range with derived bits and nibbles. Motherwords will have datatype uint[length]. Set the letter "M" into start-bit column to mark the motherword. For the derived bits, remember to use the correct datatype e.g. bits are not uint.
Note on L5: Big-Endian = N Little-Endian = Y
Note on M5: For 32 and 64-bit registers >= INT32, Float and Double Word Swap = Y
Note on N5: Lowest allowed value for the register
Note on O5: Highest allowed value for the register
Note on P5: Select the needed scale factor-reference. In the sheet Scale insert raw and engineering min and max to scale Raw-value. Remember to add decimals in the next column if needed
Note on Q5: Used for analog representation, how many decimal-points to show.
Note on S5: State which parameters should be read-only og read-and-write in IWMAC supermarket by selecting 'r' or 'rw'
Note on T5: Select which alarmlevel each alarm should get. A-alarms represents the highest level, and are the ones sent to alarm-recipients by SMS/Text-messages. B-alarms are considered medium priority, C-alarms low priority. Use the inverted alarmtypes (the ones starting with an '!' if active alarm is on numeric state/value '0'. NB! Alarms can only be added correctly to Boolean datapoints
Note on V5: IWMAC will automatically group the parameters by their datatype if nothing is set. If parameters should be grouped logically by systems, or rooms, the group name have to be added per parameter in this column

## State-Texts
State value
Reference | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
OnOff | Off | On
AutoOffOn | Auto | Off | On
NormalAlarm | Normal | Alarm
NormalFault | Normal | Fault
InactiveActive | Inactive | Active

## Scale
reference | Raw min | Raw max | Eng min | Eng max
-
x0.01 | 0 | 100 | 0 | 1
x0.1 | 0 | 10 | 0 | 1 | 'raw input' x | (Eng max -Eng min) | = 'scaled value'
x1 | 0 | 1 | 0 | 1 |  | (Raw max -Raw min)